Meeting Minutes of the

Northwestern Chester County Municipal Authority

October 23rd, 2024

The meeting was called to order by Chairman David Eames at 7:00PM.

Present for roll call were: Mr. David Eames, Mr. Michael Kern, Mr. Bill Kennedy and Mr. Eric Olsen. Absent:  Mr. Bill Ford, Mr. Matt Halvorsen

Also present were:  Mr. Derek Ink, Operator in Charge, Mr. Alex Bar, Engineer, Ms. Stephanie Kern, Administrator and Ms. Kristin Camp, Solicitor.

The minutes of the September 25th, 2024 meeting were approved on a motion by Eric Olsen and seconded by Bill Kennedy.  Motion carried.

The Treasurer's Report for September was accepted on motion by Eric Olsen and seconded by Bill Kennedy. Motion carried.

PUBLIC COMMENTS:    Sal DiGiacomo, Township Supervisor, was in attendance.

CORRESPONDENCE:  Jeff Yorick sent an email regarding the Struble Ridge tapping fees.  He is requesting to pay the old tapping fee amount of $3,400.00

per EDU.  A motion was made by Mike Kern and seconded by Bill Kennedy to

deny his request.  Motion carried.

ADMINISTRATOR'S REPORT: Stephanie Kern

Insurance Audit is complete.

SOLICITOR’S REPORT:   Kristin Camp

OPERATOR'S REPORT: Derek Ink

- Daily monthly flow for September averaged 273,000 gallons per day. The discharge monitoring report (EDMR) was submitted to DEP.

- Inspections:

-504, 514 Sativa Drive (Chestnut Ridge)

- 239 Chastain Drive (Chestnut Ridge)

3.  Sanitary Sewer Applications:

- 935 Chestnut Street

- October 7, staff removed recycle pump on daf tank unit 2 for repair due to a failed mechanical seal. Pump was taken to Whitmer Motor for repair, due to the age if a new seal is not available, we may have to replace the pump.

- October 15 Barasso excavating installed new lateral on Chestnut Street.

- We have been fighting with the sand filters for about a year with excessive run times. October 17 staff drained filter 2 due to noisy and excessive vibration from the wash water pump. While drained staff inspected the unit and found 18 of the 36 cells had sand in the underdrain section of the filter. With that I think it is time to have a more thorough inspection of the filters by Infilco Degremont, and recommend what fixes/rehab the filters need to get them running properly. Staff would also like to purchase a backup wash water pump. Staff took wash water pump on unit 2 to Whitmer Motor for repair. A motion was made by Bill Kennedy and seconded by Eric Olsen to authorize Derek Ink to purchase a backup wash water pump with the exception that the cost is not to exceed $25,000.00. Motion carried.

- Plant Upgrade:

Tertiary lagoon 1 piping is sealed off, with the lagoon completely out of service. Merrell Bros. has removed the bentonite clay liner, Pac 2 contracted Geotech boring in the lagoon where the new mbbr tank will be constructed. Merrell Bros has dredged about 50% of primary lagoon 1with removing 250 dry tons of sludge. We are anticipating around 500 dry tons removed once complete.

8.  Staff received and responded to 51 PA One calls.

ENGINEER'S REPORT: Alex Bar

OLD BUSINESS:

1.  Chestnut Ridge – No Update

.         2.  Act 537 –No Update

3.  Village Greene- No Update

4.  Honey Brook Estates-No Update.

5.  Pleasant View Welding – HRG report

6.  Syncarpha- Proceeding

7.  Mobile Reality 3/UMH/Struble Ridge –No Update

8.  Old Maple Inn Estates –HRG is awaiting the 3rd submission for review.

9.  WWTP upgrade/PennVest loan-HRG Report

10.  Keystone Court- HRG was notified that half of the sewer improvements

were installed without notification to HRG or NCCMA. The developer

was told by HRG that no additional improvements can be done without

HRG or NCCMA on site.  After discussion, it was decided on a motion

made by Eric Olsen and seconded by Mike Kern that the sewer

improvements that were completed , need to be exposed for inspection by

HRG.  Motion carried.

11.  Zook Molasses/Upward Investments – No update

12.  Land acquisition around West Pump Station/upgrade- HRG is continuing

to work on the application package for the grant.

13.  Twin County Business Park- HRG issued 2nd review letter to developer.

14.  Arbor’s Glen-HRG Report- No Update

15.  Honey Brook Hardware- No Update.

16.  Tri County Investment Group-No update.

17.  Calvary Church – No Update

18.  Chester County Solid Waste Authority- HRG is awaiting resubmission

from owner to review.

NEW BUSINESS:

1.  Resolution 2024-16:  Amendment to Reservation of Capacity was

approved on a motion made by Eric Olsen and seconded by Mike Kern.

Motion carried.

.       2.  Resolution 2024-17:  The acquisition of property located at 3641

Horseshoe Pike for the construction of a pump station was approved on

a motion made by Bill Kennedy and seconded by Eric Olsen.  Motion

carried.

3.  Resolution 2024-18:  Request of a Statewide Local Share Assessment

$1,000,000.00 grant for the replacement of the West Pump Station was

approved on a motion made by Mike Kern and seconded by Eric Olsen.

Motion carried.

4.  A motion was made by Eric Olsen and seconded by Bill Kennedy to

cancel the November 27th meeting and move the December 25th meeting

to December 11th.  Motion carried.

5.  A motion was made by Eric Olsen and seconded by Bill Kennedy to

approve the following invoices for submission to PennVest:

PactTwo - $226,350.00

HRG - $31,304.80

The Merrell Bros Inc. invoice for $180,330.45 was also approved for

payment, which was not submitted to PennVest.  Motion carried.

There being no further business to come before the board, a motion was made by   Mike Kern and seconded by Bill Kennedy to adjourn the meeting at 7:50 PM. Motion carried.

Respectfully submitted,

Michael Kern
       Secretary