Meeting Minutes of the

Northwestern Chester County Municipal Authority

December 11, 2024

The meeting was called to order by Chairman David Eames at 7:00PM.

Present for roll call were: Mr. David Eames, Mr. Eric Olsen, Mr. Bill Ford and Mr. Matt Halvorsen. Absent:  Mr. Michael Kern and Mr. Bill Kennedy.

Also present were:  Mr. Derek Ink, Operator in Charge, Mr. Alex Bar, Engineer, Ms. Stephanie Kern, Administrator.

The minutes of the October 23rd, 2024 meeting were approved on a motion by Eric Olsen and seconded by Matt Halvorsen.  Motion carried.

The Treasurer's Report for October & November was accepted on motion by Eric Olsen and seconded by Bill Ford. Motion carried.

PUBLIC COMMENTS:    None

CORRESPONDENCE:  None

ADMINISTRATOR'S REPORT: Stephanie Kern

SOLICITOR’S REPORT:   Absent

OPERATOR'S REPORT: Derek Ink

- Daily monthly flow for October averaged 248,000 gallons per day. The discharge monitoring report (EDMR) was submitted to DEP. There were two exceptions to the permit, one for Ammonia Nitrogen average monthly lbs./day 18.5, (limit 13.5 lbs./day), and Ammonia Nitrogen average monthly concentration 12.9 mg/l (limit 2.7 mg/l). Daily monthly flow for November averaged 261,000 gallons per day. The discharge monitoring report (EDMR) has not been submitted to DEP. However, there is one exception to the permit for November as well. The Ammonia Nitrogen average monthly concentration 17.2 mg/l (limit 8.1 mg/l).

- November 6, our new Dep sanitarian Kaitlyn George conducted an inspection of the plant. We were sited for two items. Once for not using an NIST thermometer in refrigerator. The second for failure to collect representative samples.

- Inspections:

- 237 Chastain Drive, 535 Sativa Drive, 537 Sativa Drive (Chestnut Ridge)

- 189 Petrelia Drive (Honey Brook Estates)

Staff started working on converting chemical mix tank to electronic variable speed.

- Staff located outfall and West Force main for Syncarpha Solar. Syncarpha received zoning approval for the project and now are working on the land development plan for the project. The only concerns staff and HRG have are making sure a 20-foot right of way is kept over NCCMA lines and manholes.

- Plant Upgrade:

-Merrell Bros will have dredging completed by next week

- Pac 2 poured foundation footings for blower building, and prepped MBBR tank site for     Dutchland. Next week Dutchland will pour pad for MBBR tank.

- Staff assisted Pac 2 with plugging 20” transfer line

- Received Triple Point Piping

- Throughout Thanksgiving Day, the area experienced numerous power blips. During these outages both of the VFDs at Cupola Pump station tripped and faulted the drives for both pumps and did not reset. During the power outages a Verizon transformer was taken out which left us no phone service at the station, therefore staff never received a high-water alarm. The neighbor across the street called at 3:30 and notified me of water flowing out of the manhole in front of the station. The overflow was reported to DEP as per their requirements.

- December 2 staff pulled pump one at Grandstaff pump station due to pump failure.  Pump was delivered to Whitmer Motor Service for repair.

- Staff received our recycle pump from Whitmer Motor Service.  It has been reinstalled at DAF tank unit 2. The plant is now running at full flow capacity.

- Sand filter inspection quote from Veolia WTS Services of $8,150.

- MGK Industries has been working on punch list at Village Greene pump station for Sam in order to get the station satisfied for Authority to take dedication.

Received and responded to 106 Pa One Calls

ENGINEER'S REPORT: Alex Bar

OLD BUSINESS:

1.  Chestnut Ridge – No Update

.         2.  Act 537 –No Update

3.  Village Greene- No Update

4.  Honey Brook Estates-No Update.

5.  Pleasant View Welding – No Update

6.  Syncarpha- Proceeding

7.  Mobile Reality 3/UMH/Struble Ridge –No Update

8.  Old Maple Inn Estates – No update.

9.  WWTP upgrade/PennVest loan-HRG Report

10.  Keystone Court- HRG report.

11.  Zook Molasses/Upward Investments – No update

12.  Land acquisition around West Pump Station/upgrade- HRG has

submitted the CFA Local Share Grant Application Package. Grant

funding will not be announced until summer/fall of 2025.

It was decided to wait to insure the property until the Authority

knew what they were going to do with house on the property.

13.  Twin County Business Park- HRG issued 2nd review letter to developer.

14.  Arbor’s Glen-HRG Report- No Update

15.  Honey Brook Hardware- No Update.

16.  Tri County Investment Group-No update.

17.  Calvary Church – No Update

18.  Chester County Solid Waste Authority- No update.

NEW BUSINESS:

1.  A motion was made by Matt Halvorsen and seconded by Eric Olsen to approve the PactTwo invoice for $533,250.00 for submission to PennVest.

Motion carried.

2.  A motion was made by Eric Olsen and seconded by Matt Halvorsen to

approve the Moxie Inc. invoice for $9,585.00 for submission  to PennVest.  Motion carried.

3.  A motion was made by Matt Halvorsen and seconded by Eric Olsen to approve the HRG invoices for $38,924.20 for submission to PennVest.  Motion carried.

4.  A motion was made by Matt Halvorsen and seconded by Eric Olsen to approve the Triplepoint invoice for $516,856.00 for submission to PennVest.  Motion carried.

5.  There was a discussion about renewing the farm leases for Enos & Katie Stoltzfus and Stephen Stoltzfus.  Since Syncarpha is expecting to start their project soon, it was decided not to renew the farm leases for 2025.

There being no further business to come before the board, a motion was made by   Eric Olsen and seconded by Matt Halvorsen to adjourn the meeting at 7:50 PM. Motion carried.

Respectfully submitted,

Eric Olsen
       Assistant Secretary