Meeting Minutes of the

Northwestern Chester County Municipal Authority

February 26, 2025

The meeting was called to order by Chairman David Eames at 7:00PM.

Present for roll call were: Mr. David Eames, Mr. Eric Olsen, Mr. Bill Ford , Mr. Matt Halvorsen, Mr. Michael Kern and Mr. Bill Kennedy.

Also present were:  Mr. Derek Ink, Operator in Charge, Mr. Alex Bar, Engineer, Mr. Michael Vital, Engineer, Ms. Stephanie Kern, Administrator and Mr. Tom Oeste, Solicitor.

The minutes of the January 22nd, 2025 meeting were approved on a motion by Matt Halvorsen and seconded by Bill Kennedy.  Motion carried.

The Treasurer's Report for January was accepted on motion by Mike Kern and seconded by Eric Olsen. Motion carried.

PUBLIC COMMENTS:    None

CORRESPONDENCE:  Cindy Bailey’s Lawn Mowing Quote for 2025.

ADMINISTRATOR'S REPORT: Stephanie Kern

SOLICITOR’S REPORT:   Tom Oeste

OPERATOR'S REPORT: Derek Ink

- Daily monthly flow for averaged 311,000 gallons per day. The discharge monitoring report (EDMR) was submitted to DEP. There were 3 exceptions to the permit, Ammonia Nitrogen average monthly lbs./day 79.9, (limit 40.5 lbs./day), and Ammonia Nitrogen average monthly concentration 33.3 mg/l (limit 8.1 mg/l), total nitrogen average monthly concentration 38.9 mg/l (limit 28.8 mg/l).

- Inspections:

-222, 249,243 Chastain Drive, 307 Glasgow Drive, 517, 511 Sativa Drive, (Chestnut Ridge)

-134 Petrelia Drive (Sweetwater Farms)

-530 James Street

- Received and responded to 68 Pa one calls.

- Plant Upgrade:

- PACT has run both aeration header lines down the center of the two primary lagoons.

- Dutchland is working on completing their work in the MBBR tank.

- BSI has completed their under-slab conduit, and has begun running their conduit inside the plant.

- PACT poured the slab for aeration building, and generator pad.

- West Pump Station:

- Meeting with HRG on Friday to talk about the beginning stages of the upgrade.

- Village Green:

- Items on the punch list that still need completed before taking dedication

- Syncarpha:

- No plans to break ground in 2025, due to PPL upgrading their transmission lines.

- Renewed the lease with the farmers, for a year, and then on a year to year basis until ground is broken

- Syncarpha is submitting the Land Development plan to the township.

- Cupola:

- Both pumps have had their annual service completed

- Folks from LASA will be coming March 6th for a Station tour.

- Stevens Trade will be coming for a tour of the station, as well as the plant.

- Sand Filters:

- Price to fix the filters came in at $231,000 for parts and materials

- Price for rehabilitation came in at $102,769

- The option for PACT to remove and dispose of 24 tons of sand will cost $18,824

A motion was made by Eric Olsen and seconded by Bill Ford to go ahead with the

emergency repair on the sand filter, using Pact Two to remove and dispose the sand.

Motion carried.

- Security:

- Staff ran new conduit and electric to install two more security cameras around the facility.

- Pipe Data View:

Approval to schedule TV and Clean of the collection system for spring of 2025.

ENGINEER'S REPORT: Alex Bar

OLD BUSINESS:

1.  Chestnut Ridge – No Update

.         2.  Act 537 –No Update

3.  Village Greene- Another letter was sent to Sam Nemroff from HRG

stating remaining punch list items.

4.  Honey Brook Estates-No Update.

5.  Pleasant View Welding – A motion was made by Eric Olsen and

seconded by Bill Ford to release PVI’s escrow balance. Motion carried.

6.  Syncarpha- Proceeding

7.  Mobile Reality 3/UMH/Struble Ridge –Bought 50 tapping fees.

UMH does not want to reserve capacity for the remaining 63 units.

8.  Old Maple Inn Estates – No update.

9.  WWTP upgrade/PennVest loan-HRG Report

10.  Keystone Court- A motion was made by Eric Olsen and seconded by

Matt Halvorsen to let Derek Ink, Alex Barr and Ian Kanter pick spots at

their discretion for Keystone Court to dig up and expose lateral and main

lines including  manholes for HRG’s inspection.  Motion carried.

11.  Zook Molasses/Upward Investments – No update

12.  Land acquisition around West Pump Station/upgrade- Meeting

with operators and engineers is scheduled to begin designs.

13.  Twin County Business Park-No Update.

14.  Arbor’s Glen-HRG Report- No Update

15.  Honey Brook Hardware- No Update.

16.  Tri County Investment Group-No update.

17.  Calvary Church – No Update

18.  Chester County Solid Waste Authority- No update.

NEW BUSINESS:

1.  A motion was made by Matt Halvorsen and seconded by Mike Kern to

approve the Stephen Stoltzfus Farm Lease Agreement.  Motion carried.

2.  A motion was made by Mike Kern and seconded by Eric Olsen to approve the Enos & Katie Stoltzfus Farm Lease Agreement.  Motion carried.

3.  A motion was made by Matt Halvorsen and seconded by Eric Olsen to approve the Pact Two payment #5 for $660,758.40 for submission to PennVest.  Motion carried.

4.  A motion was made by Bill Ford and seconded by Eric Olsen to approve the Moxie Mechanical payment #4 for $22,140.00 for submission to PennVest.  Motion carried.

5.  A motion was made by Mike Kern and seconded by Bill Kennedy to approve Change Order #1 for a decrease in the contract cost for Merrell Bros., Inc. in the amount of $223,649.45.  Motion carried.

6.  A motion was made by Mike Kern and seconded by Bill Ford to approve the Merrell Bros., Inc. final payment of $72,422.56.  This payment is from authority funds.  Motion carried.

7.  A motion was made by Mike Kern and seconded by Bill Ford to approve the 2025 quote for Cindy Bailey’s Lawn Service.  Motion carried.

8.  A motion was made by Matt Halvorsen and seconded by Mike Kern to apply for the CFA(Commonwealth Financing Authority) small water & sewer grant for $500,000.00 to be used for the West Pump Station Upgrade.

Motion carried.

There being no further business to come before the board, a motion was made by   Bill Ford and seconded by Mike Kern to adjourn the meeting at 7:55 PM. Motion carried.

Respectfully submitted,

Michael Kern
       Secretary