Meeting Minutes of the

Northwestern Chester County Municipal Authority

March 26, 2025

The meeting was called to order by Vice Chairman Bill Ford at 7:00PM.

Present for roll call were: Mr. David Eames, Mr. Eric Olsen, Mr. Bill Ford, Mr. Matt Halvorsen, Mr. Michael Kern and Mr. Bill Kennedy.

Also present were:  Mr. Derek Ink, Operator in Charge, Mr. Alex Bar, Engineer, Ms. Stephanie Kern, Administrator and Ms. Kristin Camp, Solicitor.

The minutes of the February 26th, 2025 meeting were approved on a motion by Eric Olsen and seconded by Bill Kennedy.  Motion carried.

The Treasurer's Report for February was accepted on motion by Mike Kern and seconded by Eric Olsen. Motion carried.

PUBLIC COMMENTS:    None

CORRESPONDENCE:  None

ADMINISTRATOR'S REPORT: Stephanie Kern

SOLICITOR’S REPORT:   Kristin Camp

OPERATOR'S REPORT: Derek Ink

- Daily monthly flow for February averaged 338,000 gallons per day. The discharge monitoring report (EDMR) was submitted to DEP. There were 3 exceptions to the permit, Ammonia Nitrogen average monthly lbs./day 81.0, (limit 40.5 lbs./day), and Ammonia Nitrogen average monthly concentration 34.7 mg/l (limit 8.1 mg/l), total nitrogen average monthly concentration 39.4 mg/l (limit 28.8 mg/l).

- Inspections:

- 526, 509 Sativa Drive (Chestnut Ridge)

- 245, 241 Chastain Drive (Chestnut Ridge)

- 132, 128 Sycamore Drive (Honey/Struble Ridge)

- 620 James Street (Borough)

- Received and responded to 55 Pa one calls.

- Plant Upgrade:

- MBBR tank passed leak test

- Blower Building Structural steel and roof installed

- Pact 2 continues to haul in fill dirt for around MBBR tank

- BSI Electric has all new conduit installed inside plant

- West Pump Station:

- In the process of re-evaluating if Gorman Rupp suction lift system is the best station design, or if submersible pump would be best suited for this application.

- Village Green:

- Need GIS mapping from developer

- Need valve replaced on pump discharge

- Need to confirm pump GPM flow now that force main has been cleaned

- Pipe Data View is scheduled for the week of May 12-14, and May 21-22.

- 2024 Chapter 94 report was submitted to Dep on March 25, 2024. Report showed that the plant annual average flow for 2024 was 376,000 gpd. The report also shows that there is no hydraulic or organic overload present, and also projects that there will be no hydraulic or organic loading capacity issues in the next five years. Plant hydraulic design capacity is rated for 600,000 gallons per day, and organic capacity is rated for 1,201 lbs./bod5 per day

- Office Property:

-paving of driveway

-Removal of old Barn

ENGINEER'S REPORT: Alex Bar

OLD BUSINESS:

1.  Chestnut Ridge – No Update

.         2.  Act 537 –No Update

3.  Village Greene- Developer is working on the punch list.

4.  Honey Brook Estates-HRG Report

5.  Syncarpha- A motion was made by Bill Ford and seconded by Matt

Halvorsen to approve the Memorandum of Lease Option Agreement and

The Lessor Estoppel Certificate.  Motion carried.

6.  Mobile Reality 3/UMH/Struble Ridge – HRG Report.

7.  Old Maple Inn Estates – No update.

8.  WWTP upgrade/PennVest loan-HRG Report

9.  Keystone Court- HRG Report.

10.  Zook Molasses/Upward Investments – No update

11.  West Pump Station/upgrade- HRG is looking into the style of Pump

Station.

12.  Twin County Business Park-No Update.

13.  Arbor’s Glen-HRG Report- No Update

14.  Honey Brook Hardware- No Update.

15.  Tri County Investment Group-No update.

16.  Calvary Church – No Update

17.  Chester County Solid Waste Authority- No update.

18.  A motion was made by Eric Olsen and seconded by Mike Kern to allow

the abandonment of 2 EDUs at 207 Cupola Road.  Motion carried.

NEW BUSINESS:

- A motion was made by Mike Kern and seconded by Matt Halvorsen to approve the Pact Two, LLC payment #6 in the amount of $990,020.20 for submission to PennVest.  Motion carried.

- A motion was made by Bill Ford and seconded by Eric Olsen to approve the Moxie Mechanical payment #5 in the amount of $3,960.00 for submission to PennVest.  Motion carried.

- A motion was made by Mike Kern and seconded by Bill Ford to approve payment #1 for BSI Electric in the amount of $143,433.94 for submission to PennVest.  Motion carried.

- A motion was made by Eric Olsen and seconded by Bill Kennedy to approve payment #6 for HRG in the amount of $110,417.48 for submission to PennVest.  Motion carried.

There being no further business to come before the board, a motion was made by   Bill Ford and seconded by Eric Olsen to adjourn the meeting at 8:00 PM. Motion carried.

Respectfully submitted,

Michael Kern
       Secretary