Meeting Minutes of the

Northwestern Chester County Municipal Authority

April 23, 2025

The meeting was called to order by Vice Chairman Bill Ford at 7:00PM.

Present for roll call were: Mr. Bill Ford, Mr. Matt Halvorsen, Mr. Michael Kern and Mr. Bill Kennedy. Absent:  Mr. Eric Olsen & Mr. David Eames.

Also present were:  Mr. Derek Ink, Operator in Charge, Mr. Alex Bar, Engineer, Ms. Stephanie Kern, Administrator and Ms. Kristin Camp, Solicitor.

The minutes of the March 26th, 2025 meeting were approved on a motion by Matt Halvorsen and seconded by Bill Kennedy.  Motion carried.

The Treasurer's Report for march was accepted on motion by Mike Kern and seconded by Matt Halvorsen. Motion carried.

PUBLIC COMMENTS:    None

CORRESPONDENCE:  None

ADMINISTRATOR'S REPORT: Stephanie Kern

SOLICITOR’S REPORT:   Kristin Camp

OPERATOR'S REPORT: Derek Ink

- Daily monthly flow for March averaged 350,000 gallons per day. The discharge monitoring report (EDMR) was submitted to DEP. There were 3 exceptions to the permit, Ammonia Nitrogen average monthly lbs./day 59.0, (limit 40.5 lbs./day), and Ammonia Nitrogen average monthly concentration 27.8 mg/l (limit 8.1 mg/l), total nitrogen average monthly concentration 35.6 mg/l (limit 28.8 mg/l).

- Inspections:

-507 Sativa Drive, 260 Chastain Drive, 422 Crenada Drive (Chestnut Ridge)

-120, 124 Sycamore Drive (Struble/Honey Ridge)

- Received and responded to 58 Pa one calls.

- Plant Upgrade:

- Pac 2 installing piping at MBBR tank, mason on site to form electrical room in blower building, Danco finishing building metal

- BSI installing conduit from blower building to new ppl pole for new electrical service

- Moxie mechanical installing heaters in blower building

- West Pump Station:

- We reconfirmed that a Gorman Rupp Station similar to Cupola will be the style of station that will replace the current set up.

- Village Green:

-Generator will not start, power systems scheduled to investigate (Bill will be forwarded)

-Shut off valve on pump 1 needs replaced

-GIS still needed

- Office Property:

-getting pricing from Lyons and Hole, Beiler Paving, and B.F. Brown Paving

-Removal of old Barn (Vintage Wood $19,310.80)

- staff will get a dumpster in and dispose of stored materials in barn and start removing bamboo

- Staff installed aerators 1,3,5 in primary 1 lagoon.

ENGINEER'S REPORT: Alex Bar

OLD BUSINESS:

1.  Chestnut Ridge – No Update

.         2.  Act 537 –No Update

3.  Village Greene- HRG Report

4.  Honey Brook Estates-HRG Report

5.  Syncarpha- No Update.

6.  Mobile Reality 3/UMH/Struble Ridge – HRG Report.

7.  Old Maple Inn Estates – No update.

8.  WWTP upgrade/PennVest loan-HRG Report

9.  Keystone Court- HRG Report.

10.  Zook Molasses/Upward Investments – No update

11.  West Pump Station/upgrade- HRG confirms that the Gorman Rupp

Lift pumps are the best solution for the West Pump Station.

12.  Twin County Business Park- HRG Report.

13.  Arbor’s Glen-HRG Report- No Update

14.  Honey Brook Hardware- No Update.

15.  Tri County Investment Group-No update.

16.  Calvary Church – No Update

17.  Chester County Solid Waste Authority- No update.

18.  Vernon MacIntyre (3766 Horseshoe Pike) – HRG has received updated

plans from the developer.

NEW BUSINESS:

- A motion was made by Mike Kern and seconded by Bill Kennedy to approve the Pact Two, LLC payment #7 in the amount of $685,900.00 for submission to PennVest.  Motion carried.

- A motion was made by Matt Halvorsen and seconded by Mike Kern to approve the Moxie Mechanical payment #6 in the amount of $4,230.00 for submission to PennVest.  Motion carried.

- A motion was made by Mike Kern and seconded by Bill Ford to approve payment #2 for BSI Electric in the amount of $97,103.38 for submission to PennVest.  Motion carried.

- A motion was made by Bill Kennedy and seconded by Mike Kern to approve payment #7 for HRG in the amount of $5,611.50 for submission to PennVest.  Motion carried.

- A motion was made by Matt Halvorsen and seconded by Bill Kennedy to approve Resolution 2025-1:  NCCMA’s request for a $1,000,000.00 grant from the PA Small Water and Sewer Program.  Motion Carried.

- A motion as made by Mike Kern and seconded by Matt Halvorsen to

make a donation of $200.00 to the Honey Brook Presbyterian Church in memory of James Dillow.  Motion carried.

- A motion was made by Mike Kern and seconded by Bill Kennedy to approve Triplepoint’s invoice #23415 in the amount of $516,856.00 for submission to PennVest.  Motion carried.

There being no further business to come before the board, a motion was made by   Mike Kern and seconded by Matt Halvorsen to adjourn the meeting at 7:45 PM. Motion carried.

Respectfully submitted,

Michael Kern
       Secretary