Meeting Minutes of the

Northwestern Chester County Municipal Authority

July 23, 2025

The meeting was called to order by Chairman David Eames at 7:00 PM.

Present for roll call were: Mr. Bill Ford, Mr. Michael Kern, Mr. Bill Kennedy, Mr. Eric Olsen, Mr. David Eames and Mr. Matt Halvorsen.

Also present were:  Mr. Derek Ink, Operator in Charge, Mr. Alex Bar, Engineer, Ms. Stephanie Kern, Administrator and Mr. Thomas Oeste, Solicitor.

The minutes of the June 25th, 2025 meeting were approved on a motion by Eric Olsen and seconded by Matt Halvosen.  Motion carried.

The Treasurer's Report for march was accepted on motion by Bill Kennedy and seconded by Eric Olsen. Motion carried.

PUBLIC COMMENTS:    None

CORRESPONDENCE: There was a request for an abandonment of an EDU at

435 Park Road.

ADMINISTRATOR'S REPORT: Stephanie Kern

SOLICITOR’S REPORT:   Thomas Oeste

OPERATOR'S REPORT: Derek Ink

- Daily monthly flow for June averaged 393,000 gallons per day. The discharge monitoring report (EDMR) was submitted to DEP. There was 1 exceptions to the permit for Ammonia Nitrogen average monthly concentration 2.73 mg/l (limit 2.7 mg/l).

- Inspections

- 306,309,311,313,315,317 Ashwood Ct (Honey Ridge)

- 104, 106, 108 Sycamore Drive (Honey Ridge)

- Received and responded to 75Pa one calls.

- June 26 due to heavy rain there were multiple pump station high water alarms, including West pump which resulted in an SSO at 257 Suplee Road, DEP was notified and non compliance report submitted.

- Plant Upgrade:

- Between July 7 and 8 Aerzen started up and tested all 4 blowers

- Triple Point arrived July 14 and installed all aerators in primary lagoons one and two, as well as all air piping in the MBBR tank, installed media in MBBR Tank. MBBR tank was then started up on July 18.

- Pact 2 installed bypass valves on Cupola and West force main’s near influent structure. They also started working on the influent structure concrete and slide gate rehabilitation.

- Pact 2 completed effluent pump room and pump and pipe work.

- BSI mount and install new mcc control panels, work on scada programming, and finished pulling wire for entire scope of project

- Office Property:

Vintage Wood started demo of barn July 1 and completed their scope of the demolition July 3. Staff then began site grading and removal of all stone from the barn.

ENGINEER'S REPORT: Alex Bar

OLD BUSINESS:

1.  Chestnut Ridge – No Update

.         2.  Village Greene- The Board decided that all the items

on the punch list made by HRG must be completed before the

pump station can be dedicated.

3.  Honey Brook Estates-No Update

4.  Syncarpha- No Update.

5.  Mobile Reality 3/UMH/Struble Ridge – No Update

6.  Old Maple Inn Estates – No update.

7.  WWTP upgrade/PennVest loan-HRG Report

8.  Keystone Court- No Update.

9.  Zook Molasses/Upward Investments – No update

10.  West Pump Station/upgrade- HRG is working on the final design.

11.  Twin County Business Park- No update.

12.  Arbor Glen – No update.

13.  Honey Brook Hardware- No update.

14.  Tri County Investment Group-No update.

15.  Calvary Church – No Update

16.  Chester County Solid Waste Authority- No update.

17.  Vernon MacIntyre (3766 Horseshoe Pike) – The updated plan will

require 3 EDUs.

NEW BUSINESS:

- A motion was made by Matt Halvorsen and seconded by Mike Kern to approve the Pact Two, LLC payment #10 in the amount of $368,015.15 for submission to PennVest.  Motion carried.

- A motion was made by Bill Ford and seconded by Eric Olsen to approve the Moxie Mechanical payment #9 in the amount of $47,941.70 for submission to PennVest.  Motion carried.

- A motion was made by Bill Kennedy and seconded by Mike Kern to approve payment #5 for BSI Electric in the amount of $374,550.75 for submission to PennVest.  Motion carried.

- The Board approved of the request of an abandonment of an EDU at 435 Park Road.

- It was decided by the Board that a contribution of $100.00 is to be made to the Burlington County Animal Shelter in the memory of Patrick Quinn.

- A motion was made by Eric Olsen and seconded by Bill Kennedy to approve Herbert, Rowland & Grubic, Inc.’s Construction Administration Supplement #1 for the Waste Water Treatment Plant Upgrade Project. Motion Carried.

There being no further business to come before the board, a motion was made by   Mike Kern and seconded by Matt Halvorsen to adjourn the meeting at 7:50 PM. Motion carried.

Respectfully submitted,

Michael Kern
       Secretary